## Setting
項目ｺｰﾄﾞ | ﾀﾌﾞ番号 | ﾀｲﾄﾙ1 | ﾀｲﾄﾙ2 | ﾀｲﾄﾙ3 | ﾀｲﾄﾙ4 | 許可可能値 | 単位 | 規定値 | 入力タイプ | 最小値 | 最大値 | 刻み | リスト項目 | SD設定ﾌｧｲﾙBYTENo
1 | 1 | DHW |  | Operation mode |  | Normal/Eco | - | Normal | 4 |  |  | - | 0:Normal/1:Eco | 000F
2 |  |  |  | DHW max. temp. |  | 40～60 | °C | 50 | 2 | 40 | 60 | 1 |  | 0003
3 |  |  |  | DHW temp. drop |  | 5～30 | °C | 10 | 2 | 5 | 30 | 1 |  | 0006
4 |  |  |  | DHW max. operation time |  | 30～120 | mins | 60 | 2 | 30 | 120 | 1 |  | 0009
5 |  |  |  | DHW mode restriction |  | 30～120 | mins | 30 | 2 | 30 | 120 | 1 |  | 000C
177 |  |  |  | DHW recharge |  | Standard/Large | - | Standard | 4 |  |  | - | 0:Standard/1:Large
6 |  | Legionella prevention |  | Active |  | Yes/No | - | Yes | 4 |  |  | - | 0:Yes/1:No | 0000
7 |  |  |  | Hot water temp. |  | 60～70 | °C | 65 | 2 | 60 | 70 | 1 |  | 0012
8 |  |  |  | Frequency |  | 1～30 | days | 15 | 2 | 1 | 30 | 1 |  | 0015
9 |  |  |  | Start time |  | 0:00～23:00 | - | 3:00 | 3 | 0:00 | 23:00 | 1:00 |  | 0018
10 |  |  |  | Max. operation time |  | 1～5 | hours | 3 | 2 | 1 | 5 | 1 |  | 001B
11 |  |  |  | Duration of maximum temp. |  | 1～120 | mins | 30 | 2 | 1 | 120 | 1 |  | 001E
12 | 2 | Heating / Cooling | Zone1 | Operation mode |  | Heating room temp/Heating flow temp/Heating compensation curve/Cooling flow temp | - | Heating room temp | 4 |  |  | - | 0:Heating room temp/1:Heating flow temp/2:Heating compensation curve/4:Cooling flow temp | 0000
13 |  |  |  | Heating room temp. |  | 10～30 | °C | 20 | 2 | 10 | 30 | 1 |  | 0006
14 |  |  |  | Heating flow temp. |  | 20～60 | °C | 45 | 2 | 20 | 60 | 1 |  | 0009
17 |  |  |  | Cooling flow temp. |  | 5～25 | °C | 15 | 2 | 5 | 25 | 1 |  | 0012
18 |  |  | Zone2 | Operation mode |  | Heating room temp/Heating flow temp/Heating compensation curve | - | Heating compensation curve | 4 |  |  | - | 0:Heating room temp/1:Heating flow temp/ 2:Heating compensation curve | 0003
19 |  |  |  | Heating room temp |  | 10～30 | °C | 20 | 2 | 10 | 30 | 1 |  | 001E
20 |  |  |  | Heating flow temp. |  | 20～60 | °C | 45 | 2 | 20 | 60 | 1 |  | 0021
160 |  |  |  | Cooling flow temp. |  | 5～25 | °C | 20 | 2 | 5 | 25 | 1 |  | 0021
24 |  | Compensation curve | Zone1 | Lo flow temp.set point | Outdoor ambient temp. | -28～35 | °C | 35 | 2 | -28 | 35 | 1 |  | 0018
25 |  |  |  |  | Flow temp. | 20～60 | °C | 25 | 2 | 20 | 60 | 1 |  | 0018
22 |  |  |  | Hi flow temp.set point | Outdoor ambient temp. | -30～33 | °C | -15 | 2 | -30 | 35 | 1 |  | 0015
23 |  |  |  |  | Flow temp. | 20～60 | °C | 50 | 2 | 20 | 60 | 1 |  | 0015
26 |  |  |  | Adjust | Outdoor ambient temp. | -29～34 | °C |  | 2 | -29 | 34 | 1 |  | 001B
27 |  |  |  |  | Flow temp. | 20～60 | °C |  | 2 | 20 | 60 | 1 |  | 001B
30 |  |  | Zone2 | Lo flow temp.set point | Outdoor ambient temp. | -28～35 | °C | 35 | 2 | -28 | 35 | 1 |  | 002A
31 |  |  |  |  | Flow temp. | 20～60 | °C | 25 | 2 | 20 | 60 | 1 |  | 002A
28 |  |  |  | Hi flow temp.set point | Outdoor ambient temp. | -30～33 | °C | -15 | 2 | -30 | 35 | 1 |  | 0027
29 |  |  |  |  | Flow temp. | 20～60 | °C | 40 | 2 | 20 | 60 | 1 |  | 0027
32 |  |  |  | Adjust | Outdoor ambient temp. | -29～34 | °C |  | 2 | -29 | 34 | 1 |  | 002D
33 |  |  |  |  | Flow temp. | 20～60 | °C |  | 2 | 20 | 60 | 1 |  | 002D
39 | 3 | Holiday |  | DHW |  | Active/Non active | - | Non active | 4 |  |  | - | 0:Active/1:Non active | 0000
40 |  |  |  | Heating/Cooling |  | Active/Non active | - | Active | 4 |  |  | - | 0:Active/1:Non active | 0000
45 |  |  | Zone1 | Heating room temp. |  | 10～30 | °C | 15 | 2 | 10 | 30 | 1 |  | 0009
46 |  |  |  | Heating flow temp. |  | 20～60 | °C | 35 | 2 | 20 | 60 | 1 |  | 000C
44 |  |  |  | Cooling flow temp. |  | 5～25 | °C | 25 | 2 | 5 | 25 | 1 |  | 0012
47 |  |  | Zone2 | Heating room temp. |  | 10～30 | °C | 15 | 2 | 10 | 30 | 1 |  | 0015
48 |  |  |  | Heating flow temp. |  | 20～60 | °C | 25 | 2 | 20 | 60 | 1 |  | 0018
158 |  |  |  | Cooling flow temp. |  | 5～25 | °C | 25 | 2 | 5 | 25 | 1 |  | 0018
161 | 4 | Schedule timer | Schedule2 period setting from |  |  | /Jan./Feb./Mar./Apr./May/June/July/Aug./Sept./Oct./Nov./Dec. | - |  | 4 |  |  | - | 0:/1:Jan./2:Feb./3:Mar./4:Apr./5:May/6:June/7:July/8:Aug./9:Sept./10:Oct./11:Nov./12:Dec. | 0000～
162 |  |  | Schedule2 period setting to |  |  | /Jan./Feb./Mar./Apr./May/June/July/Aug./Sept./Oct./Nov./Dec. | - |  | 4 |  |  | - | 0:/1:Jan./2:Feb./3:Mar./4:Apr./5:May/6:June/7:July/8:Aug./9:Sept./10:Oct./11:Nov./12:Dec. | 0000～
37 |  |  | Schedule timer1 | DHW1 |  |  |  |  | 8 |  |  |  |  | 0000～
36 |  |  |  | Cooling1(Zone1) |  |  |  |  | 6 |  |  |  |  | 0000～
153 |  |  |  | Cooling1(Zone2) |  |  |  |  | 6 |  |  |  |  | 0000～
34 |  |  |  | Heating1(Zone1) |  |  |  |  | 7 |  |  |  |  | 0000～0066
35 |  |  |  | Heating1(Zone2) |  |  |  |  | 7 |  |  |  |  | 0000～0066
38 |  |  | Schedule timer2 | DHW2 |  |  |  |  | 8 |  |  |  |  | 0000～
156 |  |  |  | Cooling2(Zone1) |  |  |  |  | 6 |  |  |  |  | 0000～
157 |  |  |  | Cooling2(Zone2) |  |  |  |  | 6 |  |  |  |  | 0000～
154 |  |  |  | Heating2(Zone1) |  |  |  |  | 7 |  |  |  |  | 0000～0066
155 |  |  |  | Heating2(Zone2) |  |  |  |  | 7 |  |  |  |  | 0000～0066
50 | 5 | Initial settings |  | °C/°F |  | °C/°F | - | °C | 4 |  |  | - | 0:°C/1:°F | 0003
51 |  |  |  | Temp. display |  | Room/DHW tank/Room&DHW tank /Off | - | OFF | 4 |  |  | - | 0:OFF/1:Room/2:Tank/3:Room&Tank | 0006
52 |  |  |  | Contact number |  |  |  |  | 10 |  |  |  |  | 0009～0012
53 |  |  |  | Time display |  | hh:mm/hh:mm AM/AM hh:mm | - | hh:mm | 4 |  |  | - | 0:hh:mm/1:hh:mm AM/2:AM hh:mm | 0015
84 | 6 | Service menu | Heat source setting |  |  | Standard/Heater/Boiler/Hybrid | - | Standard | 4 |  |  | - | 0:Standard/1:Heater/2:Boiler/3:Hybrid | 003C
112 |  |  | Pump speed | DHW |  | 1～5 | - | 5 | 2 | 1 | 5 | 1 |  | 0039
183 |  |  |  | Heating/Cooling |  | 1～5 | - | 5 | 2 | 1 | 5 | 1
108 |  |  | Auxiliary setting | Economy settings for pump. | On/Off | On/Off | - | ON | 4 |  |  | - | 1:ON/0:OFF | 001B
109 |  |  |  |  | Time before pump switched off (3 - 60 mins) | 3～60 | mins | 10 | 2 | 3 | 60 | 1 |  | 001E
85 |  |  |  | Electric heater(Heating) | On (used)/Off (not used) | On (used)/Off (not used) | - | ON | 4 |  |  | - | 1:ON/0:OFF | 0027
86 |  |  |  |  | Electric heater delay timer (5 - 180 mins) | 5～180 | mins | 30 | 2 | 5 | 180 | 1 |  | 002A
172 |  |  |  | Electric heater(DHW) | Booster heater On (used)/Off (not used) | On (used)/Off (not used) | - | ON | 4 |  |  | - | 1:ON/0:OFF | 002D
87 |  |  |  |  | Immersion heater On (used)/Off (not used) | On (used)/Off (not used) | - | ON | 4 |  |  | - | 1:ON/0:OFF | 0030
88 |  |  |  |  | Electric heater delay timer (15 - 30 mins) | 15～30 | mins | 15 | 2 | 15 | 30 | 1 |  | 0030
89 |  |  |  | Mixing valve | Running (10 - 240 secs) | 10～240 | secs | 120 | 2 | 10 | 240 | 1 |  | 0033
90 |  |  |  |  | Interval (1 - 30 mins) | 1～30 | mins | 4 | 2 | 1 | 30 | 1 |  | 0036
170 |  |  |  | Flow sensor | Minimum(0 - 100L/min) | 0～100 | L/min | 5 | 2 | 0 | 100 | 1 |  | 0033
171 |  |  |  |  | Maximum(0 - 100L/min) | 0～100 | L/min | 100 | 2 | 0 | 100 | 1 |  | 0036
180 |  |  |  | Analog output | Interval (1 - 30 mins) | 1～30 | mins | 5 | 2 | 1 | 30 | 1
184 |  |  |  |  | Priority (Normal/High) | Normal/High | - | Normal | 4 |  |  | - | 0:Normal/1:High
111 |  |  | Operation setting | Freeze stat function | Outdoor ambient temp. | 3～20 | °C | 5 | 2 | 3 | 20 | 1 |  | 0024
113 |  |  |  | Simultaneous operation (DHW/Heating) | On/Off | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF | 003F
114 |  |  |  |  | Outdoor ambient temp. (-30 - +10°C) | -30～10 | °C | -15 | 2 | -30 | 10 | 1 |  | 0042
117 |  |  |  | Cold weather function | On/Off | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF | 004B
118 |  |  |  |  | Outdoor ambient temp. (-30 - -10°C) | -30～-10 | °C | -15 | 2 | -30 | -10 | 1 |  | 004E
173 |  |  |  | Room temp. control(Heating) | Mode | Normal/Fast | - | Normal | 4 |  |  | - | 0:Normal/1:Fast | 0051
91 |  |  |  |  | Temp. control interval (10 - 60 mins) | 10～60 | mins | 10 | 2 | 10 | 60 | 10 |  | 0051
92 |  |  |  |  | Flow temp. range Max. temp. (35 - 60°C) | 35～60 | °C | 50 | 2 | 35 | 60 | 1 |  | 0057
93 |  |  |  |  | Flow temp. range Min. temp. (20 - 45°C) | 20～45 | °C | 30 | 2 | 20 | 45 | 1 |  | 0054
137 |  |  |  | Heat pump thermo diff. adjust | On/Off | On/Off | - | ON | 4 |  |  |  | 1:ON/0:OFF
138 |  |  |  |  | Lower limit (-9 - -1°C) | -9～-1 | °C | -5 | 2 | -9 | -1 | 1
139 |  |  |  |  | Upper limit (+3 - +5°C) | 3～5 | °C | 5 | 2 | 3 | 5 | 1
94 |  |  |  | Boiler operation Hybrid settings | Outdoor ambient temp. (-15 - +10°C) | -30～10 | °C | -15 | 2 | -30 | 10 | 1 |  | 006C
95 |  |  |  |  | Priority mode (Ambient/Cost/CO2) | Ambient/Cost/CO2 | - | Ambient | 4 |  |  | - | 0:Ambient/1:Cost/2:CO2 | 0069
187 |  |  |  |  | Outdoor ambient temp. rise (+1- +5°C) | +1～+5 | °C | 3 | 2 | 1 | 5 | 1 |  | 0069
127 |  |  |  | Boiler operation Intelligent settings | Energy price Electricity (0.001 - 999 */kWh) | 0.001～999.0 | */kWh | 0.5 | 9 | 0.001 | 999 | 0.001 |  | 0000～0192
97 |  |  |  |  | Energy Price Boiler (0.001 - 999 */kWh) | 0.001～999.0 | */kWh | 0.5 | 1 | 0.001 | 999 | 0.001 |  | 0078～007B
96 |  |  |  |  | CO2 emission Electricity (0.001 - 999 kg -CO2/kWh) | 0.001～999 | kg-CO2/kWh | 0.5 | 1 | 0.001 | 999 | 0.001 |  | 0084～0087
140 |  |  |  |  | CO2 emission Boiler (0.001 - 999 kg -CO2/kWh) | 0.001～999 | kg-CO2/kWh | 0.5 | 1 | 0.001 | 999 | 0.001 |  | 008A～008D
503 |  |  |  |  | Heat pump capacity | 1-40 | kW | 11.2 | 5
98 |  |  |  |  | Boiler efficiency (25 - 150%) | 25～150 | % | 80 | 2 | 25 | 150 | 1 |  | 006F
520 |  |  |  |  | Booster heater 1 capacity (0 - 30 kW) | 0～30 | kW | 2 | 2 | 0 | 30 | 1 |  | 005D
521 |  |  |  |  | Booster heater 2 capacity (0 - 30 kW) | 0～30 | kW | 4 | 2 | 0 | 30 | 1 |  | 0060
128 |  |  |  | Floor dry up function | Target temp. Start&Finish (20 - 60°C) | 20～60 | °C | 30 | 2 | 20 | 60 | 1 |  | 017D
129 |  |  |  |  | Target temp. Max. temp. (20 - 60°C) | 20～60 | °C | 45 | 2 | 20 | 60 | 1 |  | 0180
130 |  |  |  |  | Target temp. Max. temp. period (1 - 20 days) | 1～20 | days | 5 | 2 | 1 | 20 | 1 |  | 0183
131 |  |  |  |  | Flow temp. (Increase) Temp. increase step (+1 - +10°C) | １～10 | °C | 5 | 2 | 1 | 10 | 1 |  | 0186
132 |  |  |  |  | Flow temp. (Increase) Increase interval (1 - 7 days) | 1～7 | days | 2 | 2 | 1 | 7 | 1 |  | 0189
133 |  |  |  |  | Flow temp. (Decrease) Temp. decrease step (-1 - -10°C) | -1～-10 | °C | -5 | 2 | -10 | -1 | 1 |  | 018C
134 |  |  |  |  | Flow temp. (Decrease) Decrease interval (1 - 7 days) | 1～7 | days | 2 | 2 | 1 | 7 | 1 |  | 018F
174 |  |  | Smart grid ready | DHW | Target temp(+0- +20°C) | 0～20 | °C | 0 | 2 | 0 | 20 | 1
189 |  |  |  | Heating | On/Off | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
190 |  |  |  |  | Target temp. Switch-on recommendation(20 - 60°C) | 20～60 | °C | 50 | 2 | 20 | 60 | 1
191 |  |  |  |  | Target temp. Switch-on command(20 - 60°C) | 20～60 | °C | 55 | 2 | 20 | 60 | 1
197 |  |  |  | Cooling | On/Off | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
192 |  |  |  |  | Target temp. Switch-on recommendation(5 - 25°C) | 5～25 | °C | 15 | 2 | 5 | 25 | 1
193 |  |  |  |  | Target temp. Switch-on command(5 - 25°C) | 5～25 | °C | 10 | 2 | 5 | 25 | 1
194 |  |  |  | Pump cycles | Heating (On/Off) | On/Off | - | ON | 4 |  |  | - | 1:ON/0:OFF
195 |  |  |  |  | Cooling (On/Off) | On/Off | - | ON | 4 |  |  | - | 1:ON/0:OFF
196 |  |  |  |  | Interval(10-120 min) | 10/20/30/40/50/60/70/80/90/100/110/120 | mins | 60 | 2 | 10 | 120 | 10
199 |  |  | Summer mode | On/Off |  | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
200 |  |  |  | Outdoor ambient temp. | Heating ON (4-19°C) | 4～19 | °C | 10 | 2 | 4 | 19 | 1
201 |  |  |  |  | Heating OFF (5-20°C) | 5～20 | °C | 15 | 2 | 5 | 20 | 1
202 |  |  |  | Judgement time | Heating ON (1-48 hours) | 1～48 | hours | 6 | 2 | 1 | 48 | 1
203 |  |  |  |  | Heating OFF (1-48 hours) | 1～48 | hours | 6 | 2 | 1 | 48 | 1
204 |  |  |  | Forced heating ON(-30 - 10℃) |  | -30～10 | °C | 5 | 2 | -30 | 10 | 1
178 |  |  | Water flow control | On/Off |  | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
176 |  |  | Thermo ON output |  |  | Zone1&2/Zone1/Zone2 | - | Zone1&2 | 4 |  |  | - | 0:Zone1&2/1:Zone1/2:Zone2
185 |  |  | Heat pump setting | Heat pump flow rate range | Minimum(0 - 100L/min) | 0～100 | L/min | 5 | 2 | 5 | 100 | 1
186 |  |  |  |  | Maximum(0 - 100L/min) | 0～100 | L/min | 100 | 2 | 5 | 100 | 1
205 |  |  |  | Quiet mode | Monday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
206 |  |  |  |  | Tuesday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
207 |  |  |  |  | Wednesday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
208 |  |  |  |  | Thursday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
209 |  |  |  |  | Friday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
210 |  |  |  |  | Saturday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
211 |  |  |  |  | Sunday | On/Off | - | OFF | 4 |  |  | - | 1:ON/0:OFF
212 |  |  |  |  | Start time | 0:00～23:45/All | - | All | 3 | 0:00 | 23:45 | 0:15
213 |  |  |  |  | Finish time | 0:00～23:45 | - |  | 3 | 0:00 | 23:45 | 0:15
214 |  |  |  |  | Quiet level | Normal/LV1/LV2 | - | Normal | 4 |  |  |  | 0:Normal/1:LV1/2:LV2
120 |  |  | Energy monitor settings | Electric heater capacity | Booster heater 1 capacity (0 - 30 kW) | 0～30 | kW | 2 | 2 | 0 | 30 | 1
121 |  |  |  |  | Booster heater 2 capacity (0 - 30 kW) | 0～30 | kW | 4 | 2 | 0 | 30 | 1
163 |  |  |  |  | Immersion heater capacity (0 - 30 kW) | 0～30 | kW | 0 | 2 | 0 | 30 | 1
181 |  |  |  |  | Analog output(0 - 30 kW) | 0～30 | kW | 0 | 2 | 0 | 30 | 1
169 |  |  |  | Delivered energy adjustment | (-50 - +50%) | -50～+50 | % | 0 | 2 | -50 | 50 | 5
166 |  |  |  | Water pump input | Pump1 | 0～200 | W | *** | 2 | 0 | 200 | 1
167 |  |  |  |  | Pump2 | 0～200 | W | 0 | 2 | 0 | 200 | 1
168 |  |  |  |  | Pump3 | 0～200 | W | 0 | 2 | 0 | 200 | 1
182 |  |  |  |  | Pump4 | 0～200 | W | 72 | 2 | 0 | 200 | 1
164 |  |  |  | Electric energy meter |  | 0.1/1/10/100/1000 | pulse/kWh | 1 | 4 |  |  |  | 0.1:0.1/1:1/10:10/100:100/1000:1000
165 |  |  |  | Heat meter |  | 0.1/1/10/100/1000 | pulse/kWh | 1 | 4 |  |  |  | 0.1:0.1/1:1/10:10/100:100/1000:1000
135 |  |  | External input settings | Demand control (IN4) | Heat source OFF/Boiler operation | Heat source OFF/Boiler operation | - | Boiler operation | 4 |  |  |  | 0:Heat source OFF/1:Boiler operation | 0192
136 |  |  |  | Outdoor thermostat (IN5) | Heater operation/Boiler operation | Heater operation/Boiler operation | - | Boiler operation | 4 |  |  |  | 0:Heater operation/1:Boiler operation | 0192
198 |  |  | Heater capacity restriction |  |  | Inactive/HeaterOFF/Level1/Level2 | - | Inactive | 4 |  |  | - | 0:Inactive/1:HeaterOFF/2:Level1/3:Level2

## InputType
1 | テキスト(直接入力する数値)
2 | コンボ(数値)
3 | コンボ(時間)
4 | コンボ(テキスト)
5 | コンボ(HeatPump)
6 | Cooling設定画面起動ボタン
7 | Heating設定画面起動ボタン
8 | DHW設定画面起動ボタン
9 | Price(Schedule)設定画面起動ボタン
10 | 連絡先(MAX16桁、数値/スペース/ハイフン/プラス)
11 | 日付(直接入力orコンボ)